## Failure Mode Assumptions
Failure Key | Total | Failure Area | Failure Mode | Failure Area w/Mode
Belts - Worn:Age of belt:Replaced belt | 138 | Belt | Wear-out | Belt:Wear-out
BELT WORN:AGE OF BELT:RPL BELT | 55 | Belt | Wear-out | Belt:Wear-out
BELTS:WORN:AGE OF BELT | 40 | Belt | Wear-out | Belt:Wear-out
Belts - Worn:Worn pulleys:Replaced pulley and belt | 16 | Belt | Wear-out | Belt:Wear-out
BELT CRACKED:AGE OF BELT:RPL BELT | 8 | Belt | Wear-out | Belt:Wear-out
BELT WORN:WORN PULLEYS:RPL PULL N BELT | 8 | Belt | Wear-out | Belt:Wear-out
BELTS:CRACKED:AGE OF BELT | 6 | Belt | Wear-out | Belt:Wear-out
BELTS:WORN:WORN PULLEYS | 4 | Belt | Wear-out | Belt:Wear-out
BELT WORN:OUT OF ALIGNMNT:RPL BELT | 3 | Belt | Alignment | Belt:Alignment
Belts - Cracked:Age of belt:Replaced belt | 3 | Belt | Wear-out | Belt:Wear-out
BELTS:FATIGUE:AGE OF BELT | 3 | Belt | Wear-out | Belt:Wear-out
Belts - Worn:Age of belt:Other | 2 | Belt | Wear-out | Belt:Wear-out
BELT BROKEN:AGE OF BELT:RPL BELT | 1 | Belt | Wear-out | Belt:Wear-out
BELT CRACKED:WORN PULLEYS:RPL PULL N BELT | 1 | Belt | Wear-out | Belt:Wear-out
BELT WORN:: | 1 | Belt | Wear-out | Belt:Wear-out
Belts - Broken:Age of belt:Replaced belt | 1 | Belt | Wear-out | Belt:Wear-out
Belts - Broken:Faulty belt:Replaced belt | 1 | Belt | Wear-out | Belt:Wear-out
Belts - Worn:Fan bearings seized:Replace belts and bearings | 1 | Belt | Wear-out | Belt:Wear-out
Belts - Worn:Motor bearings seized:Replace belts and motor | 1 | Belt | Wear-out | Belt:Wear-out
BELTS:CRACKED:WORN PULLEYS | 1 | Belt | Wear-out | Belt:Wear-out
Equip - Static Pressure Below SP:Coil Dirty:Clean Dirty Strainer | 1 | Coil | Duty-cycle | Coil :Duty-cycle
Damper - EAD Hunting:Damper controls:Code review and update | 1 | Damper Controls | Hunting | Damper Controls:Hunting
Damper - EAD Hunting:Damper controls:Rectify Code | 1 | Damper Controls | Hunting | Damper Controls:Hunting
Damper - OAD Hunting:Damper controls:Code fault | 1 | Damper Controls | Hunting | Damper Controls:Hunting
Damper - OAD Hunting:Damper controls:Code review and update | 1 | Damper Controls | Hunting | Damper Controls:Hunting
Damper - OAD Hunting:Damper controls:Rectify Code | 1 | Damper Controls | Hunting | Damper Controls:Hunting
Damper - RAD Hunting:Damper controls:Code review and update | 1 | Damper Controls | Hunting | Damper Controls:Hunting
Damper - RAD Hunting:Damper controls:Tune control loop | 1 | Damper Controls | Hunting | Damper Controls:Hunting
Sensor: SAP Unexpected Value:Damper controls:Dampers seized | 1 | Damper Controls | Seized | Damper Controls:Seized
Damper - Seized:Age:Replace Damper | 9 | Damper Mechanical | Wear-out | Damper Mechanical:Wear-out
Damper - Seized:Environmental Factor:Replace Damper | 9 | Damper Mechanical | Seized | Damper Mechanical:Seized
Damper - Seized:Environmental Factor:Replaced Linkages | 5 | Damper Mechanical | Seized | Damper Mechanical:Seized
Damper - Seized:Age:Replaced Linkages | 4 | Damper Mechanical | Wear-out | Damper Mechanical:Wear-out
Damper - Seized:Age:Damper link broken | 2 | Damper Mechanical | Wear-out | Damper Mechanical:Wear-out
Damper - Seized:Environmental Factor:Damper link broken | 2 | Damper Mechanical | Seized | Damper Mechanical:Seized
:Environmental Factor:Replace Damper | 1 | Damper Mechanical | Duty-cycle | Damper Mechanical:Duty-cycle
Damper - RAD Hunting:Environmental Factor:Damper link broken | 1 | Damper Mechanical | Broken | Damper Mechanical:Broken
Damper - Seized:: | 1 | Damper Mechanical | Seized | Damper Mechanical:Seized
Damper - Seized:Actuator broken:Actuator motor burnout | 1 | Damper Mechanical | Broken | Damper Mechanical:Broken
Damper - Seized:Actuator broken:Actuator slipping on shaft | 1 | Damper Mechanical | Broken | Damper Mechanical:Broken
Damper - Seized:Environmental :Replace Damper | 1 | Damper Mechanical | Seized | Damper Mechanical:Seized
:Age of pulley:Replace pulley and belts | 1 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
Fan - Bearings seized:Age:Change bearings | 20 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
FAN BB NOISY:AGE:RPL BEARINGS | 6 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
FAN ALIGNMENT:CLEANING ISSUE:REPLACE FAN | 3 | Fan Bearing | Alignment | Fan Bearing:Alignment
Fan - Bearings noisy:Age:Replace fan | 2 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
Fan - Bearings seized:Age:Replace fan and motor | 2 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
Fan - Bearings noisy:Age:Replace bearings | 1 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
Fan - Bearings noisy:Age:Replace fan and motor | 1 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
Fan - Bearings noisy:Fan bearings seized:Replace fan | 1 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
Fan - Bearings noisy:Internal VSD fan not working:Replace VSD | 1 | Fan Bearing | Other | Fan Bearing:Other
Fan - Bearings seized:Age:Replace bearings | 1 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
Fan - Bearings seized:Age:Replace fan | 1 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
Fan - Bearings seized:Age:Replace fan bearings | 1 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
Fan - Bearings seized:Motor bearings seized:Replace fan and motor | 1 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
Fan - Out of alignment:Fan damaged:Replace fan and motor | 1 | Fan Bearing | Alignment | Fan Bearing:Alignment
FAN ALIGNMENT:BLADE BROKEN:REPLACE FAN | 1 | Fan Bearing | Alignment | Fan Bearing:Alignment
FAN BB NOISY:AGE:OTHER | 1 | Fan Bearing | Wear-out | Fan Bearing:Wear-out
Filters - BMS alarm:Normal Fouling:Replaced pre filters | 159 | Filter | Fouling | Filter:Fouling
Filters - Found in PM:Normal Fouling:Replaced pre filters | 49 | Filter | Fouling | Filter:Fouling
Filters - Analytics:Normal Fouling:Replaced pre filters | 38 | Filter | Fouling | Filter:Fouling
Filters - BMS alarm:Normal Fouling:Replaced pre and main filters | 14 | Filter | Fouling | Filter:Fouling
Filters - Found in PM:Normal Fouling:Replaced pre and main filters | 11 | Filter | Fouling | Filter:Fouling
Filters - BMS alarm:Prefilter displaced:Replaced pre filters | 7 | Filter | Other | Filter:Other
Filters - BMS alarm:Normal Fouling:Replaced main filters | 6 | Filter | Fouling | Filter:Fouling
:Normal Fouling:Replaced pre filters | 4 | Filter | Fouling | Filter:Fouling
Filters - Analytics:Normal Fouling:Replaced pre and main filters | 4 | Filter | Fouling | Filter:Fouling
Filters - Analytics:Prefilter displaced:Replaced pre filters | 4 | Filter | Other | Filter:Other
Filters - BMS alarm:Environmental :Replaced pre filters | 3 | Filter | Duty-cycle | Filter:Duty-cycle
FLTR IN PM:NRML FOULING:RPL PRE FILTERS | 3 | Filter | Fouling | Filter:Fouling
FLTR IN PM:NRML FOULING:RPL PRE MN FLTR | 3 | Filter | Fouling | Filter:Fouling
Filters - BMS alarm:Environmental Factor:Replaced pre filters | 2 | Filter | Duty-cycle | Filter:Duty-cycle
Filters - Found in PM:Environmental Factor:Replaced pre filters | 2 | Filter | Duty-cycle | Filter:Duty-cycle
Filters - Analytics:Normal Fouling:Replaced main filters | 1 | Filter | Fouling | Filter:Fouling
Filters - BMS alarm:Normal Fouling:Filter out of place | 1 | Filter | Fouling | Filter:Fouling
Filters - Found in PM:Environmental Factor:Replaced pre and main filters | 1 | Filter | Duty-cycle | Filter:Duty-cycle
Filters - Found in PM:Normal Fouling:Replaced carbon filters | 1 | Filter | Fouling | Filter:Fouling
FLTR BMS ALARM:NRML FOULING:RPL PRE FILTERS | 1 | Filter | Fouling | Filter:Fouling
FLTR BMS ALARM:NRML FOULING:RPL PRE MN FLTR | 1 | Filter | Fouling | Filter:Fouling
FLTR OTHER:NRML FOULING:RPL PRE FILTERS | 1 | Filter | Fouling | Filter:Fouling
MTR BEAR NOISE:AGE:RPL BEARINGS | 8 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
MTR BEAR NOISE:AGE:REPLACE MOTOR | 7 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
MOTOR:BEARINGS NOISY:AGE | 6 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings noisy:Age:Replace motor | 4 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings seized:Age:Replace motor | 4 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings noisy:Age:Replace bearings | 3 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings noisy:Age:Replace bearings and realign belts | 3 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
MTR BEAR NOISE:AGE:OTHER | 3 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings noisy:Age:Replace belts and bearings | 2 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings noisy:Age:Replace motor and belts | 2 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings noisy:Electropitting from VSD eddy current:Replace bearings | 2 | Motor Bearing | Electro-pitting | Motor Bearing:Electro-pitting
Motor - Bearings noisy:Electropitting from VSD eddy current:Replace bearings and realign belts | 2 | Motor Bearing | Electro-pitting | Motor Bearing:Electro-pitting
Motor - Bearings seized:Age:Replace bearings | 2 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings seized:Age:Replace bearings and retension belts | 2 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings noisy:Age:Replace bearings and retension belts | 1 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings noisy:Age:Replace fan and motor | 1 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings noisy:Motor bearings seized:Replaced motor and realigned belts | 1 | Motor Bearing | Seized | Motor Bearing:Seized
Motor - Bearings noisy:Winding Age:Replaced motor | 1 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings seized:Age:Replace bearings and realign belts | 1 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Bearings seized:Age:Replaced motor | 1 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - Down to earth:Motor bearings seized:Replace motor | 1 | Motor Bearing | Ground Fault | Motor Bearing:Ground Fault
MTR BEAR NOISE:AGE:OTHER CONTRACT | 1 | Motor Bearing | Wear-out | Motor Bearing:Wear-out
Motor - High amps:Winding Age:Replace motor | 2 | Motor Electrical | High Current | Motor Electrical:High Current
Motor - Down to earth:Power spike:Replace motor | 1 | Motor Electrical | Ground Fault | Motor Electrical:Ground Fault
Motor - Down to earth:Winding Age:Replace motor and realign belts | 1 | Motor Electrical | Ground Fault | Motor Electrical:Ground Fault
Motor - Down to earth:Winding Age:Replaced motor | 1 | Motor Electrical | Ground Fault | Motor Electrical:Ground Fault
Motor - Harmonics:Winding Age:Replace motor | 1 | Motor Electrical | High Current | Motor Electrical:High Current
Motor - Hot:Winding Age:Replaced motor | 1 | Motor Electrical | High Current | Motor Electrical:High Current
MOTOR:DOWN TO EARTH:OTHER | 1 | Motor Electrical | Ground Fault | Motor Electrical:Ground Fault
MTR HIGH AMPS:POWER SPIKE:OTHER | 1 | Motor Electrical | Power | Motor Electrical:Power
MOTOR PULLEY:WORN PULLEY:AGE OF PULLEY | 16 | Motor Mechanical | Wear-out | Motor Mechanical:Wear-out
Pulley - Motor pulley worn:Worn pulleys:Replaced pulley and belt | 16 | Motor Mechanical | Wear-out | Motor Mechanical:Wear-out
PLLY MTR WORN:AGE OF PULLEY:RPL PULL N BELT | 6 | Motor Mechanical | Wear-out | Motor Mechanical:Wear-out
PLLY MTR WORN:AGE OF PULLEY:RPL PULLEY | 6 | Motor Mechanical | Wear-out | Motor Mechanical:Wear-out
Pulley - Motor pulley worn:Age of pulley:Replace pulley | 6 | Motor Mechanical | Wear-out | Motor Mechanical:Wear-out
Pulley - Motor pulley cracked:Age of belt:Replaced pulley and belt | 1 | Motor Mechanical | Wear-out | Motor Mechanical:Wear-out
Pulley - Motor pulley worn:Age of pulley:Replaced pulley and belt | 1 | Motor Mechanical | Wear-out | Motor Mechanical:Wear-out
Other:Other:Other | 133 | Other |  | Other
OTHER:OTHER:OTHER CONTRACT | 1 | Other |  | Other
BROKEN:: | 77 | Other |  | Other
Sensor: Pressure Switch Faulty:Faulty Sensor:Replaced Sensor | 33 | Sensor | Faulty | Sensor:Faulty
Sensor: SAP Unexpected Value:Out of calibration:Calibrate Sensor | 12 | Sensor | Out-of-Calibration | Sensor:Out-of-Calibration
Sensor: RARH Unexpected Value:Out of calibration:Calibrate Sensor | 5 | Sensor | Out-of-Calibration | Sensor:Out-of-Calibration
Sensor: SAT Unexpected Value:Out of calibration:Calibrate Sensor | 3 | Sensor | Out-of-Calibration | Sensor:Out-of-Calibration
Sensor: ZT Flatlining:Faulty Sensor:Replaced Sensor | 2 | Sensor | Flatlining | Sensor:Flatlining
Sensor: CO2 Unexpected Value:Out of calibration:Calibrate Sensor | 1 | Sensor | Out-of-Calibration | Sensor:Out-of-Calibration
Sensor: OAT Flatlining:Out of calibration:Calibrate Sensor | 1 | Sensor | Out-of-Calibration | Sensor:Out-of-Calibration
Sensor: Pressure Switch Faulty:Cut Cable:Run New Cable | 1 | Sensor | Harness | Sensor:Harness
Sensor: Pressure Switch Faulty:Faulty Sensor:Sensor calibration | 1 | Sensor | Faulty | Sensor:Faulty
Sensor: Pressure Switch Faulty:SAP Sensor:Replaced Sensor | 1 | Sensor | Faulty | Sensor:Faulty
Sensor: RARH Flatlining:Out of calibration:Calibrate Sensor | 1 | Sensor | Out-of-Calibration | Sensor:Out-of-Calibration
Sensor: RARH Flatlining:Out of calibration:Replace Sensor | 1 | Sensor | Out-of-Calibration | Sensor:Out-of-Calibration
Sensor: SAP Flatlining:Faulty Sensor:Replaced Sensor | 1 | Sensor | Out-of-Calibration | Sensor:Out-of-Calibration
Sensor: SAP Unexpected Value:Other:Other | 1 | Sensor | Out-of-Calibration | Sensor:Out-of-Calibration
Sensor: ZT Flatlining:Cut Cable:Run New Cable | 1 | Sensor | Harness | Sensor:Harness
Sensor: ZT Flatlining:Other:Other | 1 | Sensor | Flatlining | Sensor:Flatlining
Sensor: ZT Flatlining:Sensor Disconnected:Reconnected Sensor | 1 | Sensor | Flatlining | Sensor:Flatlining
Sensor: ZT Unexpected Value:Sensor getting heat from equipment (TV, Printer etc):Relocate sensor | 1 | Sensor | Unexpected Value | Sensor:Unexpected Value
Sensor: ZT Unexpected Value:Sensor getting heat from equipment (TV, Printer etc):Relocated sensor | 1 | Sensor | Unexpected Value | Sensor:Unexpected Value
STATIC PRESSURE:SAP SENSOR: | 1 | Sensor | Faulty | Sensor:Faulty
Equip - Static Pressure Below SP:Faulty Sensor:Replaced Sensor | 1 | Sensor | Faulty | Sensor:Faulty
Equip - Static Pressure Below SP:SAP Sensor:Replaced Sensor | 1 | Sensor | Faulty | Sensor:Faulty
Equip - Static Pressure Below SP:Sensor Disconnected:Found Cut and Repaired | 1 | Sensor | Faulty | Sensor:Faulty
:: | 736 | Unknown |  | Unknown
:Other:Other | 2 | Unknown |  | Unknown
HHW VLV OPEN:VALVE IN MANUAL:VALVE AUTO BAS | 1 | Valve Mechanical | Open | Valve Mechanical:Open
Valve - HHWV Hunting:Valve controls:Tune control loop | 5 | Valve Controls | Tuning | Valve Controls:Tuning
Valve - CHWV Hunting:Valve controls:Tune control loop | 3 | Valve Controls | Tuning | Valve Controls:Tuning
Valve - HHWV Passing:Valve stuck:Valve replaced | 15 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve - CHWV No Flow:Valve stuck:Valve replaced | 13 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve - CHWV Passing:Valve stuck:Valve replaced | 12 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve - HHWV No Flow:Valve stuck:Valve replaced | 9 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve - CHWV Passing:Actuator broken:Actuator replaced | 4 | Valve Mechanical | Broken | Valve Mechanical:Broken
Valve - CHWV Passing:Valve stuck:replace faulty valve actuator | 4 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve - CHWV Passing:CHW Valve stuck:Valve replaced | 3 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve - CHWV No Flow:CHW Valve stuck:Valve replaced | 2 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve - HHWV No Flow:Valve actuator not driving:replace faulty valve actuator | 2 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve- CHWV Open When Fan Off:Valve stuck:Valve replaced | 2 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve - CHWV No Flow:Actuator broken:Actuator replaced | 1 | Valve Mechanical | Broken | Valve Mechanical:Broken
Valve - CHWV Passing:Actuator broken:Valve replaced | 1 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve - CHWV Passing:CHW Valve stuck:Replaced Sensor | 1 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve - CHWV Passing:Valve broken:Valve replaced | 1 | Valve Mechanical | Broken | Valve Mechanical:Broken
Valve - HHWV No Flow:HHW Valve stuck:Valve replaced | 1 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
Valve - HHWV No Flow:Valve broken:Valve replaced | 1 | Valve Mechanical | Broken | Valve Mechanical:Broken
Valve - HHWV Passing:Valve broken:Valve replaced | 1 | Valve Mechanical | Broken | Valve Mechanical:Broken
VLV CHW PASS:ACTUATOR BRK:ACTUATOR REPL | 1 | Valve Mechanical | Broken | Valve Mechanical:Broken
VLV CHW PASS:VALVE BROKEN:VALVE REPLACED | 1 | Valve Mechanical | Broken | Valve Mechanical:Broken
VLV CHW PASS:VALVE STUCK:VALVE REPLACED | 1 | Valve Mechanical | Stuck | Valve Mechanical:Stuck
VLV HHW NO FLOW:ACTUATOR DRIVE:RPL VLV ACTUATR | 1 | Valve Mechanical | Broken | Valve Mechanical:Broken
Valve - HHWV No Flow:Other:Other | 1 | Valve Other |  | Valve Other
VLV HHW PASS:: | 1 | Valve Other |  | Valve Other
VSD - Fault:VSD failed causing motor burn out:Replace VSD | 2 | VSD |  | VSD
VSD - Fault:Internal VSD fan not working:Replace VSD | 1 | VSD |  | VSD
VSD FAULT:FAN NOT WORKING:REPLACE FAN | 1 | VSD |  | VSD
VSD - Speed Fixed:VSD BAS manual:Placed back to auto | 1 | VSD Controls |  | VSD Controls
VSD - Speed Fixed:VSD BAS manual:Tune control loop | 1 | VSD Controls |  | VSD Controls
VSD SPEED:SAP SENSOR:SENSOR CALIBR | 1 | VSD Controls |  | VSD Controls